## 2KVA
SHENZHEN NEW COMPUTER TECHNOLOGY SYSTEMS (NCTS) LIMITED COMPANY
新计算机科技系统（NCTS）有限公司
深圳市龙岗区布吉诚信华庭2栋6B
www.ncts.co
Online Ups 2KVA / 1.6KW
MODEL |  | NCTS-NU2K4
PICTURE
● Load power factor is 0.8, adaptive for the develplent trend fo electrical ● Equipment and the load capacity is more strong ● Active input power factor correction (PFC), input power factor is over 0.98 ● Wide input voltage and frequency range, adaptive for extreme adverse grid environment of remote areas ● It can be connected with generators ● Zero transfer time effective ensures the safety and reliability of load operation
Specification |  | Single Phase In & Out
Rated output capacity |  | 2KVA/1.6KW
Rated | Rated voltage | 220VAC
AC input | Input voltage range | 115-300VAC±5
| Input frequency range | (45-55)±0.5Hz
| bypass voltage | 80VACx(1±5%)-285VACx(1±5%)
Battery Input | battery group voltage | 48V
| battery method | 4pcs of 12v 7.5ah batteries
| backup time(half/full) | Backup time 30 mins at load 0.5kw.
| maximum input current when power on | <150% of rated current
| battery charging time | 5-6 hours can charge to 90%(standard)
AC output | Output voltage | 220VAC±1%(invert output)
| Output frequency | 50±5Hz(when AC input is normal) 50Hz±1% (when ac inout is abnormal )
| wave form | sine wave THD<3%( linear load) sine waveTHD<8%(Nonlinear load)
| output power factor | 0.8
| Overload ability | 130% load lasting not less than 30s,Recovery point is 90% load
| Output current peak coefficient | 3:01
| Transfer time between AC and Battery | 0ms
Communication and monitoring functions |  | RS232(can transfer to 485，Smart slot(can expand to SNMP,SMS and other monitoring methods)
Tower | N.W(KG) | 24.04
| G.W(KG) | 26.49
| Unit Size(W X H X D)mm | 460*192*333
| Carton Size(W X H X D)mm | 612*327*485
Business Terms
Production ability |  | 200 Piece/Pieces per Day
Delivery time | Sample delivery time | 2 days
| Order delivery time | 21 days
Delivery port |  | SHENZHEN
Application area |  | Widely used in financial, telcom, govenment, traffic, manufacture, education etc.
Certification |  | ISO9001, ISO14001, CE, ROHS