## 3KV
Online Ups 3KVA/ 2.4KW
MODEL |  | NCTS-NU3K6
PICTURE
● Load power factor is 0.8, adaptive for the develplent trend fo electrical ● Equipment and the load capacity is more strong ● Active input power factor correction (PFC), input power factor is over 0.98 ● Wide input voltage and frequency range, adaptive for extreme adverse grid environment of remote areas ● It can be connected with generators ● Zero transfer time effective ensures the safety and reliability of load operation
Specification |  | Single Phase In & Out
Rated output capacity |  | 3KVA/2.4KW
Rated | Rated voltage | 220VAC
AC input | Input voltage range | 115-300VAC±5
| Input frequency range | (45-55)±0.5Hz
| bypass voltage | 80VACx(1±5%)-285VACx(1±5%)
Battery Input | battery group voltage | 72V
| battery method | Internal
| backup time(half/full) | half load≥10 minutes，full load≥5minutes(standard)
| maximum input current when power on | <150% of rated current
| battery charging time | 5hours can charge to 90%(standard) depend on the capacity of external battery group(long-running)
AC output | Output voltage | 220VAC±1%(invert output)
| Output frequency | 50±5Hz(when AC input is normal) 50Hz±1% (when ac inout is abnormal )
| wave form | sine wave THD<3%( linear load) sine waveTHD<8%(Nonlinear load)
| output power factor | 0.8
| Overload ability | 130% load lasting not less than 30s,Recovery point is 90% load
| Output current peak coefficient | 3:01
| Transfer time between AC and Battery | 0ms
Communication and monitoring functions |  | RS232(can transfer to 485，Dry node，Smart slot(can expand to SNMP,SMS and other monitoring methods)
Tower | N.W(KG) | 22.89
| G.W(KG) | 25.38
| Unit Size(W X H X D)mm | 460*192*333
| Carton Size(W X H X D)mm | 612*327*485
Business Terms
Production ability |  | 200 Piece/Pieces per Day
Delivery time | Sample delivery time | 2 days
| Order delivery time | 21 days
Delivery port |  | SHENZHEN
Application area |  | Widely used in financial, telcom, govenment, traffic, manufacture, education etc.
Certification |  | ISO9001, ISO14001, CE, ROHS